## Protection Burden Check
Secondary Burden Check Calculation
1. Input Parameters
CT Rated Burden Sn (VA) | 30
Rated Secondary Current In (A) | 1
Protection Relay Burden (VA/pc) | 12
Number of Meters (pcs) | 1
Copper Resistivity ρ (Ω·mm²/m) | 0.0175
Secondary Conductor Cross-section S (mm²) | 2.5
Capacity Margin Factor k | 0.8
Actual Secondary Cable Length of This Project L_act (m) | 10
2. Check Calculation
Total Protection Burden Sm (VA)
Burden Available for Secondary Conductor Sw (VA)
Allowable Secondary Conductor Resistance R (Ω)
Max. Allowable Secondary Cable Length L_allow (m)
Check Conclusion
Notes: ① Allowable resistance R = (Sn − Σ meters) / In², i.e. the conductor resistance available for the VA remaining after deducting the meter/relay burden, referred to the rated secondary current; ② Allowable cable length L_allow = R × S / ρ × k, where k is the capacity margin factor (includes allowance for terminal/contact resistance); ③ If the actual secondary cable length of this project ≤ L_allow, the CT rated VA burden requirement is met.

## Metering Burden Check
Secondary Burden Check Calculation
1. Input Parameters
CT Rated Burden Sn (VA) | 10
Rated Secondary Current In (A) | 1
Instrument Burden (VA/pc) | 5
Number of Meters (pcs) | 1
Copper Resistivity ρ (Ω·mm²/m) | 0.0175
Secondary Conductor Cross-section S (mm²) | 2.5
Capacity Margin Factor k | 0.8
Actual Secondary Cable Length of This Project L_act (m) | 10
2. Check Calculation
Total Protection Burden Sm (VA)
Burden Available for Secondary Conductor Sw (VA)
Allowable Secondary Conductor Resistance R (Ω)
Max. Allowable Secondary Cable Length L_allow (m)
Check Conclusion
Notes: ① Allowable resistance R = (Sn − Σ meters) / In², i.e. the conductor resistance available for the VA remaining after deducting the meter/relay burden, referred to the rated secondary current; ② Allowable cable length L_allow = R × S / ρ × k, where k is the capacity margin factor (includes allowance for terminal/contact resistance); ③ If the actual secondary cable length of this project ≤ L_allow, the CT rated VA burden requirement is met.

## CT Selection Parameters
CT Selection Parameter Table (Current Transformers)
No. | CT Model | Rated Secondary Current (A) | Accuracy Class (Protection) | Accuracy Class (Metering) | Rated Burden (VA) | Application | Max. Allowable Secondary Cable Length (m) | Check Conclusion
1 | See system diagram | 1 | 5P20 |  | 30 | Protection
2 | See system diagram | 1 |  | 0.2SFS5 | 10 | Metering
Notes:
1. This table is a framework for CT selection parameters. The ratio (rated primary current), CT model, accuracy class (5P/10P, etc.) and bay/equipment name shall be supplemented and confirmed according to the project primary system and protection/metering requirements.
2. "Max. Allowable Secondary Cable Length" is calculated in the "Secondary Burden Check" sheet (this data: Sn = 20 VA, secondary current 5 A, meter 1 VA × 1, conductor 2.5 mm², factor 0.8, allowable length = 86.86 m).
3. Check principle: if the actual secondary circuit cable length of this project ≤ the allowable length, the CT rated VA burden requirement is met; otherwise it is not met, and the CT rating must be increased, the conductor cross-section increased, or the cable shortened.
4. When protection and metering are checked separately, verify the total secondary circuit burden (meters + conductors) against the rated burden VA corresponding to each accuracy class.